## amortisman
AMORTIZATION TABLE
IF THE IRRIGATION WATER IS SUPPLIED FROM MUNICIPAL WATER |  | Daily water required | Monthly water required | Yearly water required | Unit Price of Municipal Water | Yearly Total Water Use Cost
UNIT |  | m³/day | m³/month | m³/year | € | €/year
VALUE |  | 70.00 | 2,100 | 14,700 | 1.5900 | 23,373
IF THE IRRIGATION WATER IS SUPPLIED FROM WWTP | WWTP CAPEX |  | Amortization Time
UNIT | € |  | Year
VALUE | 42,548 |  | 1.82
In | 22 | Months, the WWTP is amortizing itself.
*** "Unit Price of Municipal Water = 1.5900 €/m³" is given for comparison purposes.

## bilgi_sayfasi
Global Tech LLC
70 m³/day (People Equivalent) Capacity - Discharge to Nature
Rotating Biological Contactor (RBC) Sewage Treatment Plant (STP) Offer
PROJECT INFO
| Hydraulic Load | : 70 m³/day
| Organic Load | : 24.50 kg/day (70 m³/day x 350 mg/l)
| Elimination of BOD in Pre Treatment | : 8.09 kg/day ( 33% )
| Treated Organic Load in PlanetDISK® RBC Unit | : 16.42 kg/day
| Wastewater Temperature | : Min 15°C-Max 32°C
| Accepted Temperature | : 19 °C
| Wastewater Retention Time in PlanetDISK® RBC Unit | : 1.54 hours (>45 minutes minimum)
*These parameters are directly given by client. / chosen according to our experiences and literature reviews.
Wastewater Source
Only domestic wastewater from toilets, sinks, shower, dishwash and laundry. Wastewater should not contain any chemicals which is harmful for the bacteria inside wastewater. Rainwater and swimming pool water which may contain chlorine and chemicals should not be allowed into the ST system. Fat, Oil and Grease (FOG) should not be allowed into the system. Wastewater from kitchens definitely should pass through oil traps in kitchens.
Proposed System
· 1 PlanetDISK® MX 1 units - 114 disks of 2.05 m diameter disks, GRP (fiber glass) housing.
· TOTAL 114 disks x 6.6 m² x 1 units = 752.4 m² surface area.
· 1 LS 15 Lamella Separator final sedimentation tank, GRP (fiberglass) body.
· TOTAL 15 m² x 1 units = 15 m² lamella surface area.
Disk Surface Area Calculation
π x r x r x 2 sides x 114 disks/unit -> 3.14 x 1.025 x 1.025 x 2 x 114 = 752.2 m²/unit

## capex
CAPEX
Global Tech LLC |  |  |  |  | Offer Number : 0346
Offer Reference Number : YDD R0 07 08 2026 1 MX 1 70 25 114
No | Description | Piece | Unit Price | Total Price | Discount rate | Total Price after Discount
1. | MECHANICAL EQUIPMENT
1.1. | Physical Treatment Units (Primary Treatment)
1.1.1. | Coarse and Fine Screen Options
1.1.1.1. | Manually Cleaned Coarse Screen | 1 | 912.00 € | 912.00 € | %5 | 866.40 €
1.1.1.2. | Manually Cleaned Fine Screen | 1 | 958.00 € | 958.00 € | %5 | 910.10 €
1.1.2. | Grit-Oil Trap Plates | 4 | 126.00 € | 504.00 € | %5 | 478.80 €
1.1.3. | Feeding Pump (1 duty + 1 standby) - City Pumps Ranger 10 35 | 2 | 542.30 € | 1,084.60 € | %5 | 1,030.37 €
1.2. | Biological Treatment Units (Secondary Treatment)
1.2.1. | PlanetDISK® MX 1 RBC Unit; - Epoxy Painted AISI 1045 (C45) Carbon Steel Solid Shaft, - Wet Parts SS304 Stainless and Galvanized Coated Steel, - 114 disk / unit per Shaft, - Disk Surface Area 752.40 m² / unit | 1 | 32,036.00 € | 32,036.00 € | %25 | 24,027.00 €
1.2.2. | LS_15 Lamella Separator Final Clarifier Tank | 1 | 7,224.00 € | 7,224.00 € | %25 | 5,418.00 €
1.2.3. | smt 100A Final Clarifier Tank Sludge Pump | 1 | 395.85 € | 395.85 € | %5 | 376.06 €
2. | CIVIL WORKS
2.0.1. | Screen and Grit-Oil Trap Channel | ALL CIVIL WORKS WILL BE DONE BY CLIENT
2.0.2. | First Primary Sedimentation Tank
2.0.3. | Second Primary Sedimentation Tank
2.0.4. | Equalization Tank
3. | INSTALLATION MATERIAL
3.0.1. | All piping and electrical installation works | 1 | 3,817.00 € | 3,817.00 € | %5 | 3,626.15 €
4. | ELECTRICAL WORKS
4.0.1. | PlanetDISK® Control Panel | 1 | 6,121.00 € | 6,121.00 € | %5 | 5,814.95 €
5. | TRANSPORTATION
5.0.1. | 40' HC Container | 1 | 13,027.00 € | Optional | %0 | Optional
5.0.2. | Truck | 1 | 0.00 € | Optional | %0 | Optional
TOTAL |  |  |  | 53,052.45 € | Total Discount | 10,504.62 €
*Optional and Supply Locally equipment are not included in the total price. |  |  |  | Grand Total Discounted Price |  | 42,547.83 €
* V.A.T. , All Other Expenses and Taxes are EXCLUDED
* EXWORKS PlanetTEK Kocaeli Gebze Factory
* Validity : 30 days
Supply locally : equipment should be obtained locally for better warranty conditions.

## ekipman_tablosu
MECHANICAL EQUIPMENTS
Manually Cleaned Coarse Screen
Quantity | 1 Unit
Bar Spacing | 30 mm
Material | Galvanized ST37 Carbon Steel
Type | Bar or perforated type screen
Manually Cleaned Fine Screen
Quantity | 1 Unit
Bar Spacing | 10 mm
Material | Galvanized ST37 Carbon Steel
Type | Bar or perforated type screen
Grit-Grease Trap Baffles
Quantity | 4 Units
Material | Fiberglass (GRP) or Polypropylene or Composite
Dimension | 1000 x 1000 mm
Equalization Tank Feed Pumps
Quantity | 1 Duty + 1 Standby
Capacity | 2.9 m³/h @ 5.9 mSS
Motor | 0.8 kW
Type | Submersible
Brand | City Pumps Ranger 10 35
Material | Cast Iron Body
PlanetDISK® MX RBC Unit - With Lid
Quantity | 1 Unit(s)
Disk Diameter | 2.05 m
Motor Power | 1 x 0.37 kW
Surface Area per Disc | 6.6 m² / disc
Number of Discs per Unit | 114 discs / unit
Minimum Total Disc Area | 752.4 m²
Rotation Speed | 3 – 4 rpm
Unit Dimensions [L x W x H] | 3,350 x 2,370 x 2,650 mm
Discs | PP (Polypropylene), Virgin Material, Single Piece Disc, Thickness: 1.5 mm - 2 mm
Solid Shaft | Epoxy Painted AISI 1045 (C45) Carbon Steel, diameter: 85 mm
Body | Fiberglass (GRP)
Chassis | Powder Coated Carbon Steel
Wetted Parts | AISI 304 Stainless Steel
RBC Unit Manufacturer | PlanetTEK Environmental and Water Wastewater Treatment Technologies Inc.
Motor Manufacturer | WAT or equivalent
Gearbox Manufacturer | PGR or equivalent
Blower
Quantity | 1 Unit
Capacity | 15 m³/h @ 200 mbar
LS 15 Lamella Separator Final Sedimentation Tank
Quantity | 1 Unit(s)
Manufacturing Material | GRP Body & Powder Coated Carbon Steel Chassis
Lamella Plate Area | 15 m²/tank
Tank Volume | 2 m³/tank
Manufacturer | PlanetTEK Inc.
Cleaning | The sludge accumulated at the bottom is automatically discharged via the sludge pump. When necessary, lamella surfaces are manually washed with pressurized water.
Final Clarifier Tank Sludge Pump
Quantity | 1 Unit(s)
Manufacturer | Sumak or Equivalent
Capacity | 10 m³/hour @ 8.1 mSS
Motor | 0.8 kW
Type | Centrifugal Type
CIVIL WORKS
Screen Channel
Quantity | 1 Unit
Capacity | 3 m³ wet volume
Material | Reinforced Concrete
Retention Time | 30 minutes at peak flow rate of 5.8 m³/h
Primary Clarifier Tank
Quantity | 1 Unit
Capacity | 15 m³ wet volume
Material | Reinforced Concrete
Retention Time | 2.5 hours at peak flow rate of 5.8 m³/h
Secondary Clarifier Tank
Quantity | 1 Unit
Capacity | 12 m³ wet volume
Material | Reinforced Concrete
Retention Time | 2 hours at peak flow rate of 5.8 m³/h
Equalization Tank
Quantity | 1 Unit
Capacity | 12 m³ wet volume
Material | Reinforced Concrete
Retention Time | 2 hours at peak flow rate of 5.8 m³/h

## enerji_isletme
ENERGY OPERATION COST
Total Hydraulic Load | 70.00 m³/hour |  | Unit Installed Power | Total Installed Power | Power Consumed | Daily Working | Electricity Consumption
Energy Price for 1 kW.hour | 13.00 € cent
MECHANICAL EQUIPMENTS |  | Unit | kW | kW | % | hour | kW.hour/day
Physical Treatment Units (Primary Treatment)
Equalization Tank Feed Pump |  | 1 | 0.80 | 0.80 | 90% | 24 | 17.28
Biological Treatment Units (Secondary Treatment)
PlanetDISK® MX RBC Unit |  | 1 | 0.37 | 0.37 | 90% | 24 | 7.99
Secondary Clarifier Sludge Pump |  | 1 | 0.80 | 0.80 | 90% | 1 | 0.72
TOTAL ELECTRICITY CONSUMPTION | [6 empty] | 25.99
Electricity consumption per 1 m³ wastewater | [5 empty] | 0.37 | kW.hour / m³
Electricity consumption per 1 m³ wastewater | [5 empty] | 4.83 | cent / m³
Electricity Consumption Cost | [5 empty] | 3.38 1,233 | € / day € / year
*** "Energy Price for kw/hour = 13 € cent" is the rate in TURKEY & given for comparison purposes

## enerji_karsilastirma
ENERGY COMPARISON of PlanetDISK® RBC vs ACTIVATED SLUDGE SYSTEM
PlanetDISK® Unit |  |  | Activated Sludge
Motor Reduction Gear |  |  |  | Blower |  | Sludge Feed Pump
MX 1 Unit Number | 1 | pieces | Number | 1 | pieces | 1 | piece
MX 1 Motor Power | 0.37 kW |  | Power | 2.00 | kW/hour | 2.20 | kW/hour
Total Power | 0.37 | kW/hour | Total Power | 2.00 | kW/hour | 2.20 | kW/hour
Power Consumption | 90% |  | Power Consumption | 90% |  | 90%
Total Actual Power to be used | 0.33 | kW | Total Actual Power to be used | 1.80 | kW | 1.98 | kW
Electricity Price | 0.13 | €/kW | Electricity Price | 0.13 | €/kW | 0.13 | €/kW
Daily Working Time | 24 | hour/day | Daily Working Time | 24 | hour/day | 4 | hour/day
Yearly Working Time | 365 | day/year | Yearly Working Time | 365 | day/year | 365 | day/year
PlanetDISK® Unit Energy Consumption | 379 € | /year | Activated Sludge Energy Consumption | 2,050 € | /year | 376 € | /year
Comparing PlanetDISK® Unit with other systems yearly, electric power saving is |  |  |  | 2,046 € /year
For 10 years electric power saving price is equal to |  |  |  | 20,464 € /10 year
and together with blower and diffusers maintenance cost, it will be approx |  |  |  | 21,000 €

## kapak
OFFER INFORMATION
Offer Number | YDD R0 07 08 2026 1 MX 1 70 25 114
Flow Rate | 70 m³/day
Influent BOD₅ | 350 mg/l
Effluent BOD₅ | 40 mg/l
Wastewater Temperature | 19 °C

## karbon_ayakizi
CARBON FOOTPRINT
Electricity Consumption Definitions |  | Unit | Electricity Consumption Definitions |  | Unit
RBC System Energy Consumption | 8.0 | kw/day | AS System Energy Consumption | 51.1 | kw/day
RBC System Energy Consumption | 2,917 | kW/year | AS System Energy Consumption | 18,659 | kW/year
CO2 Emission Coefficient | 0.43 | kg/eMWh | CO2 Emission Coefficient | 0.43 | kg/eMWh
Annual Carbon Footprint | 1.3 | ton/year | Annual Carbon Footprint | 8.0 | ton/year
Due to electricity consumption, there is an annual debt of | 57 | trees to nature. | Due to electricity consumption, there is an annual debt of | 365 | trees to nature.

## on_yillik_maliyet
PlanetDISK® DBD TECHNOLOGY vs ACTIVATED SLUDGE SYSTEM 10 YEARS TOTAL COST OF OWNERSHIP (TCO) ANALYSIS
| Initial Investment Cost (Excl. Civil Works) | Yearly Energy Cost | Yearly Operator Cost | Yearly Maintenance & Spare Parts Cost
PlanetDISK® | 42547.83 | 379.2204 | 1219 | 350
Aktif Çamur | 31910.8725 | 2425.644 | 4876 | 1050
10 Years Total Savings with PlanetDISK®: 70,000.00 €

## opex
OPERATION EXPENDITURE - OPEX
Description | Total Price
Energy Operation Cost | 1,233 € /year
Consumables and Maintenance Cost | 36 € /year
GRAND TOTAL | 1,269 € /year

## ozet_tablosu
Quotation No |  |  |  | 2026 / 0346
Quotation Reference No |  |  |  | YDD R0 07 08 2026 1 MX 1 70 25 114
Client |  |  |  | Global Tech LLC
Design Parameters
· | Wastewater Source |  |  | Only domestic wastewater from toilets, sinks, shower, dishwash and laundry.
· | Final Destination of Treated Water |  |  | Discharge to Nature
· | Hydraulic Load |  |  | 70 | m³/day
· | Hourly Flow Rate |  |  | 2.92 | m³/hour
· | Peak Flow Rate |  |  | 5.83 | m³/hour
· | Organic Load (BOD) |  |  | 25 | kg/day
· | Wastewater Temperature |  |  | 19 | °C
· | Wastewater Retention Time in PlanetDISK® RBC Unit |  |  | 1.54 | hours
· | Number of PlanetDISK® MX 1 RBC Units |  |  | 1 | units
· | Number of Disks |  |  | 114 | disks/unit
· | Disk Diameter |  |  | 2.05 | m
· | Surface Area of 1 Disk |  |  | 6.6 | m²/disk
· | Surface Area of PlanetDISK® MX 1 RBC Unit |  |  | 752.4 | m²/unit
· | Total Disk Surface Area in this Project |  |  | 752.4 | m²
· | Final Sedimentation Tank with Lamella Separator LS 15 |  |  | 1 | units
· | 1 Unit Lamella Separator Final Sedimentation Tank LS 15 |  |  | 15 | m²/unit
· | Total Lamella Surface Area in Final Sedimentation Tank LS 15 |  |  | 15 | m²
Offer content
ü | 1 | set | Manually Cleaned Coarse Screen
ü | 1 | set | Manually Cleaned Fine Screen
ü | 4 | units | Sand-Oil Trap Plates
ü | 2 | units | Equalization Tank Feed Pumps
ü | 1 | units | PlanetDISK® MX 1 RBC Unit
ü | 1 | units | PlanetDISK® MX 1 RBC Unit Cover (Fiberglass)
ü | 1 | units | LS 15 Lamella Separator Final Sedimentation Tank
ü | 1 | units | LS 15 Lamella Separator Final Sedimentation Tank Sludge Pump
Civil & Construction Works – by Client
ü | 1 | set | Piping & Electrical Works
ü | 1 | unit | PlanetDISK® Control Panel
ü | - | - | Supervision, Engineering, Commissioning & Training

## parametre
Parameter | unit | Influent (*) | Effluent (!)
Design Flow Rate (Q) | m³/d | 70 | -
Daily BOD₅ Load | kg/d | 24.50 | -
Plant Design Flow Rate | m³/h | 2.92 | -
Biochemical Oxygen Demand (BOD₅) | mg/L | 350 | 40
Chemical Oxygen Demand (COD) | mg/L | 630 | 72
Total Suspended Solids (TSS) | mg/L | 350 | <40
Oil and Grease | mg/L | ≤25 | <20
pH | - | 6 – 9 | 6 – 9
Wastewater Temperature | °C | 15 - 32 | 15 - 32
Accepted Temperature | °C | 19 | -

## sarf_malzeme
CONSUMABLES and MAINTENANCE COST
Description | Total Amount | Consumption | Unit Price | Total Price
CONSUMABLES AND MAINTENANCE EXPENSES
Biological Treatment Units (Secondary Treatment)
PlanetDISK® MX DBD Unit
Bearing Grease | 2 bearing | 0.50 kg/year.bearing | 6 €/kg | 6.00 €/year
Gearbox Oil | 1 gearbox | 7.40 lt/year.gearbox | 4 €/lt | 29.60 €/year
GRAND TOTAL |  |  |  | 35.60 €/year