## Bilgi Sayfası
Yıldız Holding
18,492.04 GPD (People Equivalent) Capacity - Irrigation / Reuse
Rotating Biological Contactor (RBC) Sewage Treatment Plant (STP) Offer
PROJECT INFO
| Hydraulic Load | : 18,492.04 GPD
| Organic Load | : 54.01 lbs/day (18,492.04 GPD x 350 mg/l)
| Elimination of BOD in Pre Treatment | : 17.82 lbs/day ( 33% )
| Treated Organic Load in PlanetDISK® RBC Unit | : 36.19 lbs/day
| Wastewater Temperature | : Min 59°F-Max 90°F
| Accepted Temperature | : 66 °F
| Wastewater Retention Time in PlanetDISK® RBC Unit | : 1.54 hours (>45 minutes minimum)
*These parameters are directly given by client. / chosen according to our experiences and literature reviews.
Wastewater Source
Only domestic wastewater from toilets, sinks, shower, dishwash and laundry. Wastewater should not contain any chemicals which is harmful for the bacteria inside wastewater. Rainwater and swimming pool water which may contain chlorine and chemicals should not be allowed into the ST system. Fat, Oil and Grease (FOG) should not be allowed into the system. Wastewater from kitchens definitely should pass through oil traps in kitchens.
Proposed System
· 1 PlanetDISK® MX 1 units - 114 disks of 6.73 ft diameter disks, GRP (fiber glass) housing.
· TOTAL 114 disks x 71.04 ft² x 1 units = 8,098.8 ft² surface area.
· 1 LS 15 Lamella Separator final sedimentation tank, GRP (fiberglass) body.
· TOTAL 161 ft² x 1 units = 161 ft² lamella surface area.
Disk Surface Area Calculation
π x r x r x 2 sides x 114 disks/unit -> 3.14 x 3.363 x 3.363 x 2 x 114 = 8,096.2 ft²/unit