## Ekipman Tablosu
MECHANICAL EQUIPMENTS
Manually Cleaned Coarse Screen
Quantity | 1 Unit
Bar Spacing | 1.18 inch
Material | Galvanized ST37 Carbon Steel
Type | Bar or perforated type screen
Manually Cleaned Fine Screen
Quantity | 1 Unit
Bar Spacing | 0.39 inch
Material | Galvanized ST37 Carbon Steel
Type | Bar or perforated type screen
Grit-Grease Trap Baffles
Quantity | 4 Units
Material | Fiberglass (GRP) or Polypropylene or Composite
Dimension | 39.4 x 39.4 in
Equalization Tank Feed Pumps
Quantity | 1 Duty + 1 Standby
Capacity | 12.9 GPM @ 19.4 ft
Motor | 0.8 kW
Type | Submersible
Brand | City Pumps Ranger 10 35
Material | Cast Iron Body
PlanetDISK® MX RBC Unit - With Lid
Quantity | 1 Unit(s)
Disk Diameter | 6.73 ft
Motor Power | 1 x 0.37 kW
Surface Area per Disc | 71.04 sq.ft / disc
Number of Discs per Unit | 114 discs / unit
Minimum Total Disc Area | 8,098.76 sq.ft
Rotation Speed | 3 – 4 rpm
Unit Dimensions [L x W x H] | 11.0 x 7.8 x 8.7 ft
Discs | PP (Polypropylene), Virgin Material, Single Piece Disc, Thickness: 1.5 mm - 2 mm
Solid Shaft | Epoxy Painted AISI 1045 (C45) Carbon Steel, diameter: 3.35 inch
Body | Fiberglass (GRP)
Chassis | Powder Coated Carbon Steel
Wetted Parts | AISI 304 Stainless Steel
RBC Unit Manufacturer | PlanetTEK Environmental and Water Wastewater Treatment Technologies Inc.
Motor Manufacturer | WAT or equivalent
Gearbox Manufacturer | PGR or equivalent
Blower
Quantity | 1 Unit
Capacity | 8.8 CFM @ 2.9 psi
LS 15 Lamella Separator Final Sedimentation Tank
Quantity | 1 Unit(s)
Manufacturing Material | GRP Body & Powder Coated Carbon Steel Chassis
Lamella Plate Area | 161.5 ft²/tank
Tank Volume | 396 GAL/tank
Manufacturer | PlanetTEK Inc.
Cleaning | The sludge accumulated at the bottom is automatically discharged via the sludge pump. When necessary, lamella surfaces are manually washed with pressurized water.
Final Clarifier Tank Sludge Pump
Quantity | 1 Unit(s)
Manufacturer | Sumak or Equivalent
Capacity | 44.0 GPM @ 26.5 ft
Motor | 0.8 kW
Type | Centrifugal Type
Recirculation Pump
Quantity | 1 Duty + 1 Standby
Capacity | 51.4 GPM @ 19.4 ft
Motor | 0.8 kW
Type | Submersible
Brand | City Pumps Ranger 10 35
Material | Cast Iron Body
Denitrification Tank Mixer
Quantity | 1 Unit(s)
Motor | 0.4 kW
Type | Submersible
Brand | ...
FeCl3 Dosing Pump
Quantity | 1 Unit(s)
Solution | Liquid Chlorine
Capacity | 1.3 GPH @ 72.5 PSI
FeCl3 Solution Tank
Quantity | 1 Unit(s)
Capacity | 53 GAL
Material | Polyethylene
Pre-Chlorination Dosing Pump
Quantity | 1 Unit(s)
Solution | Liquid Chlorine
Capacity | 1.3 GPH @ 72.5 PSI
Pre-Chlorination Solution Tank
Quantity | 1 Unit(s)
Capacity | 53 GAL
Material | Polyethylene
Filtration System Feed Pump
Quantity | 1 Duty + 1 Standby
Capacity | 17.6 GPM @ 20-30 mSS
Motor | 2.2 kW
Pump Type | Centrifugal
Filtration System Backwash Pump
Quantity | 1 Duty + 1 Standby
Capacity | 41.4 GPM @ 20-30 mSS
Motor | 2.2 kW
Pump Type | Centrifugal
Separator Filter
Quantity | 1 Unit(s)
Capacity | 17.6 GPM
Filter Type | 100 Microns
Material | AISI 304 Stainless Steel
Fully Automatic Sand Filter System with Surface Piping
Quantity | 1 Unit(s)
Flow Rate | 17.6 GPM
Filtration Velocity | 16.4-23.0 ft/hour
Valve Quantity | 5 units/tank
Valve Control | With Electric Actuator
Automation | Siemens Logo
Tank Material | Epoxy Painted ST37 Carbon Steel / FRP Tank
Piping Material | PVC
Backwash Flow Rate | 41.4 GPM
Test Pressure | 130.5 psi
Operating Pressure | 29-87 psi
Fully Automatic Active Carbon Filter System with Surface Piping
Quantity | 1 Unit(s)
Flow Rate | 17.6 GPM
Filtration Velocity | 16.4-23.0 ft/hour
Valve Quantity | 5 units/tank
Valve Control | With Electric Actuator
Automation | Siemens Logo
Tank Material | Epoxy Painted ST37 Carbon Steel / FRP Tank
Piping Material | PVC
Backwash Flow Rate | 41.4 GPM
Test Pressure | 130.5 psi
Operating Pressure | 29-87 psi
Decanter
Quantity | 1 Unit
Manufacturer | Polat or Haus
Capacity | 4.4 GPM
Motor | 7.5 kW + 4 kW
Type | Centrifugal
Sludge Feed Pump
Quantity | 1 Unit
Manufacturer | Allweiler or Equivalent
Capacity | 4.4 GPM
Motor | 1.5 kW
Pump Type | Centrifugal
Filtrate Water Pump
Quantity | 1 Unit
Manufacturer | City Pumps Ranger or equivalent
Capacity | 4.4 GPM
Motor | 0.75 kW
Pump Type | Submersible
Poly Dosing Unit
Quantity | 1 Unit
Manufacturer | PlanetTEK
Capacity | 52.8 gal/h
Motor | 1.1 kW
Type | Solution tank and dosing unit
Membrane Cassettes
Quantity | 2 Unit
Total Area | 731.9 sq ft
Dimensions | 600Wx950Lx1350H
Membrane Feed Pump
Quantity | 1 Unit
Capacity | 16.3 GPM
Motor Power | 20.0 kW
Recirculation Pump
Quantity | 1 Unit
Capacity | 12.8 GPM
Motor Power | 20.0 kW
NaOCl Dosing Pump
Quantity | 1 Unit
Capacity | 1.3 GPH
Motor Power | 0.10 kW
NaOCl Dosing Tank
Quantity | 1 Unit
Volume | 26 GAL
Material | PE
Citric Acid Dosing Pump
Quantity | 1 Unit
Capacity | 1.3 GPH
Motor Power | 0.10 kW
Citric Acid Dosing Tank
Quantity | 1 Unit
Volume | 26 GAL
Material | PE
Blower
Quantity | 1 Unit
Capacity | 24.1 CFM
Motor Power | 20.0 kW
CIVIL WORKS
Screen Channel
Quantity | 1 Unit
Capacity | 770 GAL wet volume
Material | Reinforced Concrete
Retention Time | 30 minutes at peak flow rate of 25.7 GPM
Anoxic Denitrification Tank
Quantity | 1 Unit
Capacity | 9,933 GAL wet volume
Material | Reinforced Concrete
Retention Time | 4 hours at flow rate of 41.4 GPM
Primary Clarifier Tank
Quantity | 1 Unit
Capacity | 3,850 GAL wet volume
Material | Reinforced Concrete
Retention Time | 2.5 hours at peak flow rate of 25.7 GPM
Secondary Clarifier Tank
Quantity | 1 Unit
Capacity | 3,080 GAL wet volume
Material | Reinforced Concrete
Retention Time | 2 hours at peak flow rate of 25.7 GPM
Equalization Tank
Quantity | 1 Unit
Capacity | 3,080 GAL wet volume
Material | Reinforced Concrete
Retention Time | 2 hours at peak flow rate of 25.7 GPM
Treated Water Tank
Quantity | 1 Unit
Capacity | 3,080 GAL wet volume
Material | Reinforced Concrete
Retention Time | 1 hour at peak flow rate of 25.7 GPM
Filtered Water Tank
Quantity | 1 Unit
Capacity | Tank capacity will be selected according to customer request
Material | Reinforced Concrete
Retention Time | It is recommended to choose a volume as much as the irrigation need